BlueSim Training Guide

Fixed CO2 Flooding System

Safety & Emergency

High-pressure CO2 total flooding system simulator for engine room and cargo pump room. Covers full discharge sequence, boundary damper control, and evacuation procedures per SOLAS II-2/Reg.10, FSS Code Ch.5, and IACS UR F15.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

High-pressure CO2 total flooding system simulator for engine room and cargo pump room. Covers full discharge sequence, boundary damper control, and evacuation procedures per SOLAS II-2/Reg.10, FSS Code Ch.5, and IACS UR F15.

## Key Features

72-cylinder CO2 bank with reserve tracking and pressure monitoring.

Two-zone selector (Engine Room / Cargo Pump Room) with independent valve control.

Full discharge sequence: pre-alarm, ventilation shutdown, 20-second delay, CO2 release.

CO2 concentration gauge rising to design 40% v/v with visual flooding animation.

Six boundary damper status indicators with interlock logic.

Personnel evacuation checklist interlock before discharge authorization.

Scenarios: Normal ER Flooding Drill, Abort Sequence, System Fault.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| SYSTEM CONTROL | Displays real-time system data, controls, and status indicators. |
| CO2 SYSTEM SCHEMATIC | Displays real-time system data, controls, and status indicators. |
| SYSTEM STATUS | Displays real-time system data, controls, and status indicators. |
| EVACUATION CHECKLIST | Displays real-time system data, controls, and status indicators. |
| EVENT LOG | Displays real-time system data, controls, and status indicators. |
| SYSTEM PARAMETERS | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Fixed CO2 Flooding System — Technical Reference

### Overview

A fixed high-pressure CO2 total flooding system provides fire suppression in enclosed spaces aboard vessels (engine room, cargo pump room). CO2 is stored in high-pressure cylinders at approximately 55–60 bar and is released via a series of pilot cylinders and zone selector valves into the protected space.

### Regulatory Basis

**SOLAS II-2/Regulation 10** — Fire extinguishing systems

**FSS Code Chapter 5** — Fixed gas fire-extinguishing systems

**IACS Unified Requirement F15** — CO2 systems for engine rooms

**IMO MSC/Circ.1318** — Guidelines for CO2 system maintenance

### System Components

#### Cylinder Bank

| Parameter | Value |

|-----------|-------|

| Total main cylinders | 72 |

| Reserve cylinders | 18 (25%) |

| Cylinder capacity | 45 kg CO2 each |

| Cylinder pressure | 55–60 bar (21°C) |

| Pilot cylinders | 2 per zone |

#### Zones

| Zone | Designation | Volume (m³) | CO2 Required (kg) |

|------|-------------|-------------|-------------------|

| Engine Room | ER | 2,400 | 1,680 |

| Cargo Pump Room | CPR | 420 | 294 |

#### Discharge Sequence (Automatic/Manual)

1. Pre-alarm horn activated (audible alarm in protected space)

2. Ventilation fans stopped, HVAC isolation

3. Boundary dampers close (6 dampers for ER, 2 for CPR)

4. 20-second time delay (evacuation time)

5. CO2 pilot cylinders actuated

6. Zone selector valve opens

7. Main CO2 discharge begins

8. CO2 concentration rises to >34% v/v (design: 40%)

#### Minimum Design Concentration

**34% v/v** minimum for engine rooms (FSS Code 5.1.2)

**40% v/v** design concentration (with safety factor)

Release time: 85% of required quantity within 2 minutes

### Control Modes

| Mode | Description |

|------|-------------|

| AUTO | ESD/fire alarm trigger initiates full sequence |

| MANUAL | Operator initiates via control box key |

| LOCAL | Direct manual actuation at cylinder bank |

### Safety Interlocks

Personnel-in-space check confirmation required before release

All 6 boundary dampers must confirm CLOSED before release

Engine room ventilation stop confirmation

2-key or dual-action requirement for discharge initiation

### Boundary Dampers (Engine Room)

| Damper | Location |

|--------|----------|

| D-01 | Uptake air inlet port side |

| D-02 | Uptake air inlet starboard |

| D-03 | Forced draught fans (FD-01) |

| D-04 | Forced draught fans (FD-02) |

| D-05 | Engine room skylight |

| D-06 | Emergency escape trunk |

### Alarm Setpoints

| Alarm | Tag | Level |

|-------|-----|-------|

| Cylinder pressure low | CO2-PA-001 | <50 bar |

| Zone valve fault | CO2-ZV-FAULT | Any valve fail-to-position |

| Failed release | CO2-REL-FAIL | No flow within 5s of command |

| Loss of pilot pressure | CO2-PP-LOW | <45 bar |

### Post-Discharge Procedures

1. Do NOT re-enter space until CO2 has cleared

2. Mechanical ventilation for minimum 30 minutes before entry

3. Check O2 level >20.5% v/v before entry

4. Inspect/replace discharged cylinders

5. Notify flag state and classification society

6. Record in official logbook

### Maintenance Schedule

| Task | Interval |

|------|----------|

| Cylinder weight check | 12 months |

| Pressure gauge check | 12 months |

| Pilot line pressure test | 12 months |

| Damper function test | 6 months |

| System annual survey | 12 months (class) |

| Full system test | Per class schedule |

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System