BlueSim Training Guide

Earth Fault Detection & Isolation

Electrical & Power

IT system earth fault detection and isolation training with flashing earth fault lamp, section-by-section isolation procedure, and resistance measurement display.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

IT system earth fault detection and isolation training with flashing earth fault lamp, section-by-section isolation procedure, and resistance measurement display.

## Key Features

IT insulated system with flashing earth fault lamp and resistance indicator.

20+ feeder circuits for systematic section-by-section isolation.

Phase fault indicator (A/B/C) and insulation resistance display in kΩ.

Double earth fault scenario with immediate danger indication.

Educational panel explaining why IT systems are used on ships.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| EARTH FAULT INDICATOR | Displays real-time system data, controls, and status indicators. |
| FEEDER CIRCUITS — CLICK TO ISOLATE/RESTORE | Displays real-time system data, controls, and status indicators. |
| ISOLATION LOG & PROCEDURE | Displays real-time system data, controls, and status indicators. |
| WHY IT SYSTEMS ON SHIPS | Displays real-time system data, controls, and status indicators. |
| INSULATION RESISTANCE GUIDE | Displays real-time system data, controls, and status indicators. |
| SCENARIO STATUS | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Earth Fault Detection & Isolation — Technical Reference

### Overview

Ship electrical systems use the IT (Insulated Terra / Isolated from Earth) configuration where neither pole of the supply is intentionally connected to earth. This provides continuity of supply even when a single earth fault occurs — a critical advantage at sea where loss of power could be catastrophic.

### Regulatory Basis

**IEC 60092-350** — Insulated systems: general construction and test requirements

**IACS UR E10** — Electrical installations requirements — IT systems

**SOLAS II-1/Reg.45** — Precautions against shock, fire and other electrical hazards

**IEC 60364-5-52** — Electrical installations of buildings (IT system reference)

**Classification Rules** — Earth fault monitoring requirements

### Why IT System on Ships?

| Feature | IT System | TN System (Shore) |

|---------|-----------|-------------------|

| First earth fault | System continues, alarm only | Circuit trips |

| Supply continuity | Maintained on first fault | Lost on first fault |

| Personnel shock risk | Lower on first fault | Higher |

| Fault finding | Manual isolation procedure | Fuse/CB trips — easier |

| Suitability for ships | Excellent | Poor |

The IT system allows a ship to continue essential operations (steering, propulsion, navigation) even after a first earth fault, giving time to locate and clear the fault safely.

### Earth Fault Indication

#### Earth Fault Lamp

Located on MSB and ESB panels

**Steady glow or flash:** Earth fault present

**Off:** System insulation healthy

#### Insulation Resistance Monitoring

Continuous monitoring via Ground Fault Detector (GFD)

Typical alarm setpoint: < 100 kΩ to earth

Typical trip setpoint: < 50 kΩ (for sensitive equipment)

Displayed as resistance value (MΩ or kΩ)

### Earth Fault Location Procedure

#### Method 1: Section-by-Section Isolation

1. Note which phase earth fault lamp is bright/on

2. Open each main feeder circuit breaker in turn

3. When lamp extinguishes (or insulation resistance improves significantly) → fault is in that section

4. Restore other feeders to service

5. Sub-isolate within the faulted section (sub-boards, branch circuits)

6. Repeat until faulty equipment identified

#### Method 2: Insulation Resistance Tester (Megger)

1. Isolate circuit from supply

2. Connect megger between conductor and earth

3. Apply 500V DC test voltage

4. Read insulation resistance:

- > 1 MΩ: Good

- 100 kΩ – 1 MΩ: Marginal — monitor

- < 100 kΩ: Fault present

- < 10 kΩ: Serious fault

#### Method 3: GFD Coupler (High-Frequency Injection)

Advanced systems inject HF signal into system

Coupler clamp detects which circuit carries the fault current

Non-intrusive — no need to isolate circuits

### Types of Earth Faults

#### Single Earth Fault

One conductor makes contact with earth/ship's hull

System continues to operate normally

Alarm activates

Personnel at risk if they touch the faulted conductor and are grounded

**Action:** Locate and clear at first opportunity

#### Double Earth Fault

Two conductors on different circuits touch earth simultaneously

Equivalent to a short circuit between those two points

May cause circuit breaker trips, arc, or fire

**Action:** Immediate isolation required

#### Intermittent Earth Fault

Fault appears and disappears (vibration, moisture ingress, damaged insulation)

Difficult to locate using static methods

May require continuous monitoring over time

### Common Causes on Ships

1. Moisture ingress — most common; cable glands, junction boxes

2. Mechanical damage — abrasion, pinching during cargo operations

3. High temperatures — insulation degradation near engines, exhaust

4. Aging insulation — older cables, frequent flexing

5. Water in motor windings — after bilge flooding or cleaning with hose

6. Faulty portable equipment — leads, power tools

### Safety Rules for Earth Fault Hunting

Always use rubber-soled insulating boots and gloves

Never operate MSB with known double earth fault

One person watches earth fault lamp; one person operates breakers

Keep other personnel clear of electrical equipment during fault hunting

Record all operations in the electrical log

Inform bridge/officer of watch before commencing isolation work

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System