BlueSim Training Guide

Generator Synchronising Panel

Electrical & Power

Manual and automatic generator synchronisation training with animated synchronoscope, voltage/frequency matching, and breaker closure control.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Manual and automatic generator synchronisation training with animated synchronoscope, voltage/frequency matching, and breaker closure control.

## Key Features

Animated synchronoscope with FAST/SLOW/IN SYNC needle rotation.

Governor and AVR adjustment controls for incoming generator.

Synchro-check interlock — breaker only closes within tolerance.

Auto-sync mode with live status display.

Four scenarios: Manual Sync, Auto Sync, Reverse Power Trip, Frequency Droop.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| RUNNING DG — ON BUS | Displays real-time system data, controls, and status indicators. |
| SYNCHRONOSCOPE — PHASE COMPARISON | Displays real-time system data, controls, and status indicators. |
| INCOMING DG — CONTROLS | Displays real-time system data, controls, and status indicators. |
| SYNC CONDITIONS | Displays real-time system data, controls, and status indicators. |
| POST-SYNC STATUS | Displays real-time system data, controls, and status indicators. |
| SCENARIO INFO | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Generator Synchronising Panel — Technical Reference

### Overview

Generator synchronisation is the process of connecting an incoming generator to a live busbar without causing disturbance. Correct synchronisation requires matching voltage, frequency, and phase angle between the incoming machine and the bus before closing the circuit breaker.

### Regulatory Basis

**SOLAS II-1/Reg.41** — Main source of electrical power

**IEC 60034-1** — Rotating electrical machines — Rating and performance

**IEC 60092-301** — Marine generators

**Marine Engineering practice** — Class surveyor requirements for manual sync capability

### Synchronising Conditions (The "Three Must-Match" Rule)

| Parameter | Tolerance for Breaker Close | Risk if Outside Tolerance |

|-----------|---------------------------|---------------------------|

| Voltage | ± 5V (≈ ±1% of 440V) | Magnetising current surge, voltage collapse |

| Frequency | ± 0.1 Hz (≈ ±0.17% of 60Hz) | Reverse power, speed hunting |

| Phase Angle | ± 5° | High current surge, breaker trip, mechanical shock |

### The Synchronoscope

The synchronoscope is an instrument that displays the phase difference between the incoming generator and the running bus.

**Clockwise rotation (FAST):** Incoming generator frequency > bus frequency

**Counter-clockwise rotation (SLOW):** Incoming generator frequency < bus frequency

**Stationary at 12 o'clock:** Frequencies are equal AND phase angle is 0° — CLOSE NOW

**Rule:** Always approach sync from the FAST side (slight over-frequency) so the incoming machine takes load immediately on connection

### Manual Synchronising Procedure

1. Start incoming generator; allow to reach rated speed and voltage

2. Observe synchronoscope — is it rotating fast or slow?

3. Adjust governor to match frequency (target: needle rotating slowly clockwise)

4. Adjust AVR to match voltage (target: ΔV < 5V)

5. Anticipate needle reaching 12 o'clock — close breaker at or just before 12 o'clock

6. Observe reverse power relay — should not operate

7. Transfer load gradually from running machine to incoming machine

### Auto-Synchronising

The auto-synchroniser continuously adjusts governor and AVR signals to bring the incoming machine into sync automatically. It inhibits breaker close unless all three conditions are met simultaneously.

### Post-Synchronisation

After closing the breaker:

Check for reverse power (incoming machine taking reactive load from bus = motoring)

Gradually transfer load using governor (increases kW) and AVR (adjusts kVAr sharing)

Monitor bus voltage and frequency — should remain stable

If reverse power trip operates: incoming machine was too slow at moment of closure

### Protections on Synchronising Panel

| Protection | Function |

|-----------|----------|

| Reverse power relay | Trips incoming CB if machine is absorbing power |

| Overcurrent relay | Trips on excessive current after paralleling |

| Synchro-check relay | Prevents CB close if conditions not met |

| Under/over voltage | Monitors bus and machine voltage |

| Under/over frequency | Monitors bus and machine speed |

### Common Faults

**Closing too early (leading):** Large current transient, mechanical shock to engine coupling

**Closing too late (lagging):** Reverse power trip, machine motors briefly

**Voltage mismatch high:** Circulating reactive current, possible overload

**Voltage mismatch low:** Reverse VAr, poor power factor

**Wrong phase sequence:** Never close — catastrophic damage

### Standards for STCW Competency

Per STCW Table A-III/1, officers must demonstrate:

Manual synchronisation of generators

Understanding of automatic synchronising systems

Fault diagnosis on parallel operation

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System