BlueSim Training Guide

MSB / ESB Switchboard Operation

Electrical & Power

Main Switchboard (MSB) and Emergency Switchboard (ESB) operation training with clickable breakers, bus tie control, earth fault indicators, and tripped breaker reset.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Main Switchboard (MSB) and Emergency Switchboard (ESB) operation training with clickable breakers, bus tie control, earth fault indicators, and tripped breaker reset.

## Key Features

Full MSB single-line diagram with clickable OPEN/CLOSED/TRIPPED breakers.

Emergency Switchboard with essential load feeders and auto bus transfer relay.

Earth fault indicator per switchboard section.

Bus tie breaker operation and split-bus isolation.

Four scenarios: Bus Section Fault, Emergency Bus Transfer, Tripped Breaker, Shore Power Takeover.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| MAIN SWITCHBOARD (MSB) & EMERGENCY SWITCHBOARD (ESB) | Displays real-time system data, controls, and status indicators. |
| ALARMS & STATUS | Displays real-time system data, controls, and status indicators. |
| BREAKER OPERATION LOG | Displays real-time system data, controls, and status indicators. |
| FEEDER STATUS | Displays real-time system data, controls, and status indicators. |
| SCENARIO | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## MSB / ESB Switchboard Operation — Technical Reference

### Overview

The Main Switchboard (MSB) is the central distribution hub for the ship's electrical system. The Emergency Switchboard (ESB) provides power to essential safety systems when the main system fails. Together they form the backbone of the ship's electrical distribution.

### Regulatory Basis

**SOLAS II-1/Reg.42** — Emergency source of electrical power in cargo ships

**SOLAS II-1/Reg.43** — Emergency source of electrical power in passenger ships

**SOLAS II-1/Reg.44** — Starting arrangements for emergency generators

**SOLAS II-1/Reg.45** — Precautions against shock, fire and other hazards

**IEC 60092-302** — Marine switchboards

**IEC 60092-303** — Marine automation equipment

**IACS UR E10** — Electrical installations survey

### Main Switchboard (MSB)

#### Construction

**Voltage:** 440 V AC, 3-phase, 60 Hz

**Insulation level:** IT (Insulated Terra) — no intentional earth connection

**Busbar material:** Tinned copper

**Enclosure:** IP44 minimum (IP54 in exposed locations)

**Access:** Front and rear (from insulated mat, with GRP barriers)

#### MSB Sections

| Section | Contents |

|---------|---------|

| Generator Feeders | DG1, DG2, DG3 circuit breakers + protection relays |

| Main Distribution | Feeder CBs to bow thruster, cargo pumps, compressors |

| Accommodation Feeder | Main lighting, HVAC, galley, laundry |

| Engine Room Services | Fuel transfer pumps, purifiers, fans |

| Bus Tie Panel | Bus tie breaker for split-bus operation |

| Shore Power Panel | Shore supply breaker + isolation transformer |

#### Circuit Breakers

Types used on MSB:

**ACB (Air Circuit Breaker):** Main generator/bus tie breakers — manually operated or motor-operated

**MCCB (Moulded Case CB):** Feeder circuits — thermal-magnetic protection

**MCB (Miniature CB):** Small distribution circuits

States:

**CLOSED (C):** Breaker is closed, circuit energised

**OPEN (O):** Breaker is open, circuit isolated

**TRIPPED (T):** Breaker tripped on fault — requires manual reset after fault clearance

#### Bus Tie Breaker

Connects Section A and Section B of split bus

Normally OPEN for fault isolation

CLOSED for maintenance or bus transfer

Interlocked to prevent paralleling generators via bus tie without synchronisation

### Emergency Switchboard (ESB)

#### Construction

**Voltage:** 440 V AC (fed from ESB transformer or direct DG feed)

**Location:** Above damage waterline, forward of collision bulkhead (SOLAS)

**Separation:** Fire and flooding resistant separation from MSB

**Transfer:** Automatic (bus transfer relay) and manual

#### Essential Loads on ESB

SOLAS requires minimum 18-hour supply to:

Navigation lights

Internal communication equipment (GMDSS, PA)

Fire detection and alarm systems

Fire pump (emergency)

Emergency lighting (corridors, stairways, lifeboats)

CO2/fixed fire-fighting system controls

Bilge pump (emergency)

Watertight door controls

#### Auto Bus Transfer (ABT)

When MSB voltage drops below threshold (typically 70% Un for >3s):

1. ABT relay detects loss of MSB supply

2. Emergency generator (or battery/UPS) takes over

3. ESB automatically transfers to emergency supply

4. Essential loads restored within 45 seconds (SOLAS)

### Earth Fault Indication

All switchboard sections have earth fault indicator lamps

IT system: first earth fault does not cause circuit trip but activates alarm

Earth fault panel shows which section (A/B) has fault

Engineer must locate and clear earth fault before second fault causes trip

### Breaker Operations — Safe Procedure

1. Verify load on circuit before opening

2. Check for earth fault on section

3. Operate breaker — confirm state changes on mimic

4. Test: attempt to close again (auto-reclose disabled for safety)

5. Log operation in MSB log

### Interlocks

Generator breaker interlock: prevents close unless generator is at rated speed/voltage

Bus tie interlock: prevents paralleling without synchronisation

Shore power interlock: prevents closing shore CB if generators online (reverse power protection)

ESB transfer interlock: prevents manual bypass while auto-transfer in progress

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System