BlueSim Training Guide

Power Management System (PMS)

Electrical & Power

Ship Power Management System simulation with diesel generators, busbar control, load shedding, blackout recovery, and preferential trip sequences.

# 1. Display Requirements

| Optimal Resolution | 1920 x 1080 (Full HD) |
| --- | --- |
| Minimum Resolution | 1366 x 768 |
| Aspect Ratio | 16:9 (recommended) or 16:10 |
| Browser | Chrome 90+, Firefox 90+, Edge 90+ (fullscreen recommended) |
| Input | Mouse + keyboard (touchscreen not supported) |

Note: The simulator is designed for desktop use. On screens below 980 x 600 px, a "Screen Too Small" notice will appear. For the best experience, press F11 for fullscreen mode after launching the simulator.

# 2. Simulator Overview

Ship Power Management System simulation with diesel generators, busbar control, load shedding, blackout recovery, and preferential trip sequences.

## Key Features

3x Diesel generators + emergency generator with full start/stop control.

Live kW/kVAr meters, power factor display, and load trending.

Blackout detection with automatic standby generator start.

Preferential trip panel for non-essential load shedding.

Four scenarios: Normal Load Sharing, Blackout Recovery, Preferential Trip, Shore Power Changeover.

# 3. Interface Layout

The simulator uses a multi-panel layout with the following regions:

| Panel | Purpose |
| --- | --- |
| EXIT | Displays real-time system data, controls, and status indicators. |
| GENERATOR CONTROL | Displays real-time system data, controls, and status indicators. |
| SINGLE LINE DIAGRAM — 440V MAIN BUS | Displays real-time system data, controls, and status indicators. |
| ALARMS & CONTROLS | Displays real-time system data, controls, and status indicators. |
| BUS PARAMETERS | Displays real-time system data, controls, and status indicators. |
| PREFERENTIAL TRIP PANEL | Displays real-time system data, controls, and status indicators. |
| LOAD SETPOINTS & INFO | Displays real-time system data, controls, and status indicators. |

Header Bar: Shows simulator title, regulatory reference, live clock, fullscreen toggle, and exit button.

Left Panel: System gauges, valve controls, and operational parameters.

Center Panel: P&ID schematic or main visual display (canvas/SVG).

Right Panel: Alarm management, emergency controls, and scenario buttons.

Bottom Panels: Trend charts, gas detection, scenario checklists, and supplementary data.

# 4. System Components

# 5. Training Scenarios

Scenario information will be displayed in the simulator modal on launch. Follow the on-screen checklist to complete each training objective.

# 6. Emergency Procedures

When an alarm condition occurs:

1. Identify the alarm in the Alarm Management panel (right side).

2. Acknowledge the alarm by clicking on it.

3. Assess the severity: WARNING (amber) requires monitoring; ALARM (red) requires immediate action.

4. If Emergency Shutdown (ESD) is required, press the ESD button.

5. Follow the scenario checklist for step-by-step response.

6. After resolving the condition, use the RESET button to restore normal operations.

# 7. Reference Documentation

## reference

## Power Management System (PMS) — Technical Reference

### Overview

The Power Management System (PMS) automatically controls the ship's electrical power plant to ensure safe, efficient, and continuous power supply to all consumers aboard. It manages generator start/stop, bus connections, load sharing, and protective functions.

### Regulatory Basis

**SOLAS II-1/Reg.41–46** — Main source of electrical power, emergency source, precautions against shock, fire and other hazards

**IEC 60092-301** — Electrical installations in ships — Equipment — Generators and motors

**IEC 60092-101** — Definitions and general requirements

**IACS UR E10** — Hull return system, insulated systems

**Class rules** (DNV, LR, BV, ABS) — Power plant redundancy and availability

### System Architecture

#### Generators

| Unit | Type | Rating | Voltage | Frequency |

|------|------|--------|---------|-----------|

| DG1 | Diesel Generator | 1500 kW | 440 V | 60 Hz |

| DG2 | Diesel Generator | 1500 kW | 440 V | 60 Hz |

| DG3 | Diesel Generator | 1500 kW | 440 V | 60 Hz |

| EG  | Emergency Generator | 250 kW | 440 V | 60 Hz |

#### Main Busbar

**Voltage:** 440 V AC, 3-phase

**Frequency:** 60 Hz

**Configuration:** Single bus with bus-tie option

**Protection:** Over/under voltage, over/under frequency, reverse power, differential

### Key Functions

#### 1. Load Monitoring

Continuous kW/kVAr measurement per generator

Bus voltage and frequency monitoring

Power factor display

Total load percentage indicator

#### 2. Generator Starting Sequence

1. Pre-lube oil circulation (30 sec)

2. Engine cranking (max 3 attempts)

3. Speed build-up to rated RPM

4. Voltage/frequency stabilisation

5. Ready for synchronisation

#### 3. Blackout Detection & Recovery

Busbar voltage drop below 80% rated → blackout detected

Automatic start of standby DG (within 30–45 seconds for SOLAS compliance)

Auto-close breaker on standby generator once voltage/frequency in range

Sequential restart of essential consumers

#### 4. Load Shedding

Triggered when total bus load exceeds setpoints:

**Level 1 (80% load):** Warning alarm

**Level 2 (90% load):** Non-essential load trip (accommodation AC, laundry, galley heater)

**Level 3 (95% load):** Additional non-essential loads tripped

**Overload (>100%):** Emergency load shed + standby DG start command

#### 5. Preferential Trip

Non-essential loads are tripped in sequence to prevent generator overload:

1. Accommodation Air Conditioning (est. 120 kW)

2. Laundry Equipment (est. 30 kW)

3. Galley Heater (est. 45 kW)

4. Workshop Equipment (est. 25 kW)

#### 6. Shore Power Changeover

Verify shore supply parameters match ship system

Synchronise shore supply to bus

Close shore breaker, open DG breakers

Reverse for departure

### Protection Settings

| Protection | Pickup | Time Delay |

|-----------|--------|------------|

| Overvoltage | 110% Un | 1.0 s |

| Undervoltage | 85% Un | 2.0 s |

| Overfrequency | 103% fn | 0.5 s |

| Underfrequency | 97% fn | 2.0 s |

| Reverse Power | –5% rated kW | 3.0 s |

| Overcurrent | 110% In | IDMT |

| Differential | 20% differential | Instantaneous |

### Operating Modes

**Manual:** All starts/stops and switching done by operator

**Semi-Auto:** PMS monitors and advises; operator confirms

**Full Auto:** PMS manages all generator operations autonomously

### Performance Standards

Blackout recovery time: < 45 seconds (SOLAS)

Voltage regulation: ±2.5% steady state

Frequency regulation: ±5% steady state

Load acceptance: 100% step load in < 10 seconds

### Alarms & Logs

All PMS events are time-stamped and logged. Alarms require acknowledgement. Unacknowledged alarms are indicated by audible and visual signals in accordance with SOLAS requirements.

# 8. Trainee Assessment Checklist

The instructor should verify the trainee can:

Identify all panels and their functions.

Read and interpret gauge values and colour codes.

Operate valve controls correctly.

Acknowledge and respond to alarms within appropriate time.

Execute the Emergency Shutdown procedure.

Complete at least two training scenarios with all checklist items done.

Explain the regulatory basis for the system (where applicable).

| Assessment Item | Result (Pass/Fail) | Remarks |
| --- | --- | --- |
| Scenario Completion |  |  |
| Alarm Response |  |  |
| Emergency Procedure |  |  |

Generated by BlueSim Training Guide System